## Datasheet
Doc. nr.: | [6 empty] | Flowmeter Datasheet | [13 empty] | Project number |  |  | NACAG - DeN2O
[21 empty] | Plant |  |  | Nitric Acid
[21 empty] | Section |  |  | 11 - E
| GENERAL | [13 empty] | FUNCTIONAL LOCATION
| 1 | TAG number |  |  |  |  | FIT-11E02 | [7 empty] | 52 | Service | [5 empty] | Volume flow rate in stack gas
| 2 | PID number |  |  |  |  | 11-Y-1-A | [7 empty] | 53 | Location | [5 empty] | Tail of Nitric acid plant
| 3 | Steam Number |  |  |  |  | 28"-M-11036 | [7 empty] | 54 | Hazardous area classification | [5 empty] | Class II, Division 1, Group IIC
| 4 | Hook-up drawing number |  |  |  |  | F-11E02 | [7 empty] | 55 | Minimum protection type | [5 empty] | NEMA 4X
| 5 | [13 empty] | 56
| PROCESS CONDITIONS | [13 empty] | AMBIENT CONDITIONS
| 6 |  |  |  |  | Units | Min. |  | Operat. |  |  | Max. |  |  | 57 | [5 empty] | Units
| 7 | Operating pressure |  |  |  | bara | 1.02 |  | 1.05 |  |  | 1.1 |  |  | 58 | Ambient temperature |  |  |  |  | °C | Min. | 28 |  | Max. |  | 35
| 8 | Density |  |  |  | kg/m³ |  |  | 0.8807 | [5 empty] | 59 | Humidity range |  |  |  |  | % | 80 - 95 |  |  | noncondensing
| 9 | Operating temperature |  |  |  | °C | 110 |  | 120 |  |  | 130 |  |  | 60 | Altitude |  |  |  |  | m | 5
| 10 | Viscosity |  |  |  | mPa.s |  |  | 0.0218 | [5 empty] | 61 | Corrosivity cat. (ISO 12944-2) | [5 empty] | C5-I (industrial)
| 11 | Fluid name |  |  |  |  | Tail Gas | [7 empty] | 62
| 12 | Fluid state |  |  |  |  | Gas | [7 empty] | ENCLOSURE
| 13 | Fluid contains solids |  | Abrasiveness |  |  | NO |  |  | Low |  |  |  |  | 63 | Enclosure material | [5 empty] | Stainless steel
| 14 | [13 empty] | 64 | Ingress protection | [5 empty] | NEMA 4X
| SENSOR ELEMENT / BODY | [13 empty] | 65 | Cable gland entry | [5 empty] | 1/2-14 NPT
| 15 | Element type |  |  |  |  | Annubar Flow Meter | [7 empty] | 66
| 16 | Type of pressure |  |  |  |  | Differential pressure | [7 empty] | CHEMICAL SEAL
| 17 | Operating temperature |  |  |  | °C | Min. | 120 |  | Max. |  |  | 130 |  | 67 | L- press. side | Seal type
| 18 | Burst pressure |  |  |  |  | 689,47 barg | [7 empty] | 68 |  | Seal mounting
| 19 | Process connection |  |  |  |  | Flanged | [7 empty] | 69 |  | Diaphragm exten. length
| 20 | Isolating diaphragm material |  |  |  |  | SS316L | [7 empty] | 70 |  | Seal wetted parts mat.
| 21 | Oval flange material |  |  |  |  | Stainless steel | [7 empty] | 71 |  | Seal model number
| 22 | Flow Direction |  |  |  |  | Vertical - Up | [7 empty] | 72 | H- press. side | Seal type
| 23 | Pipe size | Material |  |  |  | 28" SS 5S | [7 empty] | 73 |  | Seal mounting
| 24 | Process medium |  |  |  |  | Gases N2, O2, NOx and N2O ppm | [7 empty] | 74 |  | Diaphragm exten. length
| 25 | [13 empty] | 75 |  | Seal wetted parts mat.
| TRANSMITTER | [13 empty] | 76 |  | Seal model number
| 26 |  |  |  |  | Units | Min. |  | Operat. |  |  | Max. |  |  | 77 | Seal upper mat. |  |  | Flange mat.
| 27 | Measuring range |  |  |  | Nm³/h | 35000 |  | 38000 |  |  | 40000 |  |  | 78 | Capillary length |  |  |  | unit |  | L-side |  |  | H-side
| 28 | Calibrated span |  |  |  | % | 10% - 80% | [7 empty] | 79 | Capillary internal diameter
| 29 | Reference accuracy (% of span) |  |  |  |  | ±0,04% | [7 empty] | 80 | Capillary material
| 30 | Flow Accuracy at % regarcy |  |  |  |  | 0 ± 0,911 | [7 empty] | 81 | Capillary armor material
| 31 | Long term stability |  |  |  |  | ± 0,2% of URL for 10 years | [7 empty] | 82 | Fill fluid
| 32 | Power supply |  |  | unit |  | Min. |  |  | Max. |  |  |  |  | 83 | Process connection
| 33 | Output signal / communication |  |  |  |  | 4 - 20 mA HART 5 | [7 empty] | 84
| 34 | Rangedown |  |  |  |  | 10:1 Flow turndown | [7 empty] | NOTES
| 35 | Differential Sensor |  |  |  |  | Range 1: 0 to 25 inH2O | [7 empty] | 85
| 36 | Update Rate |  |  |  |  | 1 sec
| 37 | Fail safe action |  |  |  |  | Down Scale | [7 empty] | 86
| 38 | [13 empty] | 87
| ACCESSORIES | [13 empty] | 88
| 38 | Mounting bracket | [12 empty] | 89
| 39 | Manifold type | Manifold mat. | [11 empty] | SUPPLIER INFORMATION
| 40 | Manifold instrument connection | [12 empty] | 90 | Vendor
| 41 | Manifold process connection | [12 empty] | 91 | Manufacturer
| 42 | Other options | [12 empty] | 92 | Pressure transmitter model
| 43 | [13 empty] | 93 | Vendor stamp
| 44 | [13 empty] | 94
| 45 | [13 empty] | 95
| 46 | [13 empty] | 96
| REFERENCE DOCUMENTS/APPLICABLE SPECIFICATIONS | [13 empty] | RELIABILITY DATA
| 47 | Number |  | Rev |  | Title | [8 empty] | 97 | Fail safe detected (FIT)
| 48 | [13 empty] | 98 | Fail safe undetected (FIT)
| 49 | [13 empty] | 99 | Fail dangerous detected (FIT)
| 50 | [13 empty] | 100 | Fail dangerous undetected (FIT)
| 51 | [13 empty] | 101 | Safe failure fraction (SFF) (%)
[8 empty] | DATE |  |  | REV |  | BY | CHK |  | APP |  | SUBJECT OF REVISION
[8 empty] | 2023-08-24 |  |  | AM
| Monómeros Information confidential | [24 empty] | Page 1 of 1
Note on AU16: Corrosivity selector Exterior : C1 : Not applicable C2 : Atmospheres with low level of pollution. Mostly rural areas. C3 : Urban and industrial atmospheres, moderate SO2 pollution. Coastal areas with low salinity. C4 : Industrial areas and coastal areas with moderate salinity. C5-I : Industrial areas with high humidity and aggressive atmosphere. C5-M : Coastal and offshore areas with high salinity. Interior : C1 : Heated buildings with clean atmospheres, e.g. offices, shops, schools, hotels, ... C2 : Unheated buildings where condensation may occur, e.g. depots, sports halls, ... C3 : Production rooms with high humidity and some air pollution, e.g. food-processing plants, laundries, breweries, dairies, ... C4 : Chemical plants, swimming pools, coastal ship- and boatyards, ... C5-I : Buildings or areas with almost permanent condensation and with high pollution. C5-M : Buildings or areas with almost permanent condensation and with high pollution.
Note on Q26: Process connection selector Threaded : - G1/8" or G1/4" or G1/2" (parallel) - R1/8" or R1/4" or R1/2" (tapered) - M5 - 1/8" NPTf or 1/8" NPTm (tapered) - 1/4" NPTf or 1/4" NPTm (tapered) - 1/2" NPTf or 1/2" NPTm (tapered) Flanged : - 1" CL150 RF - 2" CL150 RF Clamped : - 1 1/2" or 2" per DIN 32676 - DN32 or DN40 per DIN 32676 - DN40 or DN50 per DIN 32676 - DN38 or DN40 or DN51 per ISO 2852 - DN40 or DN50 per DIN 11851 - DN40 or DN50 per DIN 11864-1 form A - DN42.4 or DN48.3 per DIN 11864-1 form A - 1 1/2" or 2" per DIN 11864-1 form A - DN40 or DN50 per DIN 11864-2 form A - DN42.4 or DN48.3 per DIN 11864-2 form A - 1 1/2" or 2" per DIN 11864-2 form A - DN40 or DN50 per DIN 11864-3 form A - DN42.4 or DN48.3 per DIN 11864-3 form A - 1 1/2" or 2" per DIN 11864-3 form A - VARIVENT form F or form N - NEUMO BioControl size 50 or size 65 Saddle : - for piping size 2 1/2" or 3" or 4" or 5" or 6" or 8" or 10" or 12" or 14"
Note on AU40: Process connection selector Threaded : - G1/8" or G1/4" or G1/2" (parallel) - R1/8" or R1/4" or R1/2" (tapered) - M5 - 1/8" NPTf or 1/8" NPTm (tapered) - 1/4" NPTf or 1/4" NPTm (tapered) - 1/2" NPTf or 1/2" NPTm (tapered) Flanged : - 1" CL150 RF - 2" CL150 RF Clamped : - 1 1/2" or 2" per DIN 32676 - DN32 or DN40 per DIN 32676 - DN40 or DN50 per DIN 32676 - DN38 or DN40 or DN51 per ISO 2852 - DN40 or DN50 per DIN 11851 - DN40 or DN50 per DIN 11864-1 form A - DN42.4 or DN48.3 per DIN 11864-1 form A - 1 1/2" or 2" per DIN 11864-1 form A - DN40 or DN50 per DIN 11864-2 form A - DN42.4 or DN48.3 per DIN 11864-2 form A - 1 1/2" or 2" per DIN 11864-2 form A - DN40 or DN50 per DIN 11864-3 form A - DN42.4 or DN48.3 per DIN 11864-3 form A - 1 1/2" or 2" per DIN 11864-3 form A - VARIVENT form F or form N - NEUMO BioControl size 50 or size 65 Saddle : - for piping size 2 1/2" or 3" or 4" or 5" or 6" or 8" or 10" or 12" or 14"

## Drop-down lists (hidden)
Fluid state | Fluid contains solids | Abrasiveness | Element type | Pressure type | Max. working pressure | Burst pressure | Isolating diaphragm
Solid | YES | Low | Resistive | Absolute pressure | URL | 689,47 barg | SS316L
Liquid | NO | Moderate | Piezo-resistive | Relative pressure | 51,7 barg | 758,42 barg | Alloy C-276
Gas |  | High | Piezo-electric | Differential pressure | 138 barg | 1792,64 barg | Alloy 400
Biphasic liquid/gas |  |  | Capacitive |  | 250 barg | 10000 psig | Tantalum
|  |  | Silicon resonant |  | 310 barg | 11000 psig | Gold plated Alloy 400
[5 empty] | 420 barg | 26000 psig | Gold plated SS
750 psig
2000 psig
3626 psig
4500 psig
6092 psig
Oval flange | Long term stability | Output signal | Mounting bracket | Manifold type | Manifold material | Manifold instrument connection | Manifold process connection
Stainless steel | 1 year | 4 - 20 mA | 2" pipe mounting | N/A | N/A | 1/4-18 NPTf | 1/4-18 NPTf
Cast C-276 | 2 years | 4 - 20 mA HART 5 | Wall mounting | One-way | SS 316 | 1/2-14 NPTf | 1/2-14 NPTf
Cast Alloy 400 | 5 years | 4 - 20 mA HART 7 | Panel mounting | Three-way | Alloy C-276 | 1/2-14 NPTm | 1/2-14 NPTm
Plated CS | 7 years | FOUNDATION fieldbus |  | Four-way | Alloy 400 | Flange | Flange
| 10 years | PROFIBUS PA |  | Five-way
Wireless
low power 1 - 5 Vdc HART
Other options | Approvals | Humidity | Corrosivity | Enclosure material | Ingress protection | Cable gland entry | Seal type
N/A | N/A | condensing | C1 (very low) | Aluminum polyurethane coated | IP43 | 1/2-14 NPT | N/A
Integral indicator | Calibration certificate | noncondensing | C2 (low) | Stainless steel | IP53 | M20 x 1.5 | Diaphragm screwed
Transient protection | Seal surface finish certificate |  | C3 (medium) | Polymer | IP54 | G 1/2 | Diaphragm flanged
NAMUR high alarm fail mode | Material cert. per EN 10204 3.1 |  | C4 (high) |  | IP55 |  | Diaphragm + extended flange
NAMUR low alarm fail mode | Hydrostatic test certificate |  | C5-I (industrial) |  | IP56 |  | Flanged + extended diaphragm
Wired TAG plate | NACE MR0175/ISO 15156 cert. |  | C5-M (marine) |  | IP65 |  | Diaphragm cell type
| EC Declaration of conformity |  |  |  | IP66 |  | Diaphragm clamped
| ATEX certificate |  |  |  | IP67 |  | Diaphragm in-line
| SIL1 certificate |  |  |  | IP68
| SIL2 certificate |  |  |  | NEMA 3
NEMA 4X
Seal mounting 1 | Seal mounting 2 | Diaphragm extension length | Seal wetted parts | Seal upper material | Seal flange material | Capillary ID | Capillary material
N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Direct | Flush | 50 mm | SS 316L | SS 316L | CS | 0,7 mm | SS 316L
Remote | Non-flush | 100 mm | SS 316L lined with HALAR | Brass | SS 304 | 1,1 mm | Hastelloy C-276
| Tongue | 150 mm | Hastelloy B2 | Polypropylene | SS 316 | 1,9 mm
| In pipe |  | Hastelloy C-276 | PVC | Hastelloy C-276 | 0,03 inch
|  |  | Hastelloy C4 | PVDF | Monel | 0,04 inch
|  |  | Monel 400 |  |  | 0,075 inch
Tantalum
Titanium
Uranus B6
Gold-plated Monel 400
Gold-plated SS 316
Silver
EPDM lined with PTFE
Capillary armor | Fill fluid
N/A | N/A
Stainless Steel | Silicone 200
Stainless Steel + PVC coating | Silicone 200 for vacuum
Reinforced stainless steel | Silicone 704
Silicone 704 for vacuum
Silicone 705
Silicone 705 for vacuum
Syltherm XLT
Inert (Halocarbon)
Glycerin and water
Neobee M-20
Propylene glycol and water
Ultra Therm 805
Ultra Therm 805 for vacuum